## Prameter of Generation Unit
Unit | H(s) | R(p.u) | Rated power(MW)
1,9,12,31,32 | 5.016 | 0 | 25
2,6,8,14,15,16,22, 23, 26, 33, 34, 35, 37,38, 43, 47, 48, 50 | 1.2 | 0 | 25
3,42,49 | 4.4893 | 0 | 25
4,29,36 | 2.319 | 0.0085 | 35.29
5 | 4.768 | 0.04 | 590
7,30 | 1.52 | 0 | 40
10,20,45 | 3.006 | 0.0152 | 330
11 | 3.704 | 0.0122 | 410
13,19,39 | 6.187 | 0.066 | 75
17,53 | 5.078 | 0 | 51.2
18,44 | 6.186 | 0 | 75
21,46,51 | 4.985 | 0.05 | 100
24,25 | 4.122 | 0.0214 | 233
27,28 | 2.631 | 0.0098 | 512
40 | 2.6419 | 0.006 | 835
41,52 | 4.985 | 0 | 100
54 | 2.621 | 0 | 384

## Base power
Loading Condition
| Peak |  |  | Mid |  |  | Light
Area | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
Area base power | 1105 | 1537 | 905 | 834 | 1097 | 690 | 640 | 928 | 523
System base power | 3547 |  |  | 2621 |  |  | 2091

## Power outage
Power outage scenario | Loading Condition
| Peak |  |  | Mid |  |  | Light
1 | 0 | 325 | 0 | 0 | 325 | 0 | 0 | 325 | 0
2 | 0 | 325 | 325 | 0 | 325 | 325 | 0 | 325 | 0
3 | 0 | 625 | 325 | 0 | 625 | 325 | 0 | 625 | 325
4 | 255 | 625 | 325 | 255 | 625 | 325 | - | - | -

## Input Parameter
Parameter | Definition | Value
| Nominal system frequency | 50 Hz
| Maximum deviation of the steady-state frequency | 0.5 Hz
| Minimum deviation of the steady-state frequency | -0.5 Hz
| Minimum allowable frequency | 47.5 Hz
| Maximum allowable frequency | 51.5 Hz
| Time step of SFR | 0.1 sec
D | Load damping facto | 2
| Governor time constant | 5 sec
| Time delay before activation of load shedding stage | 200ms
| Minimum load shedding per stage | 0.015 p.u
| Maximum load shedding per stage | 0.07p.u
W | Increased load shedding per stage | 0.005p.u